STANDARD FORM FOR REQUESTING INFORMATION ON PRESSURE AND CAPACITY

| Request for information from GT |  |  |  | GT’s Request ref no: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Scotia Gas Networks |  | National Grid |  |  | Wales & West Networks |  |  |  |  |  | Northern Gas Networks |  |
| 1. Details of person / organisation requesting information The Requester completes this section identifying their organisation, contact details and the person who should be sent the response from the GT or who should be contacted in the event of a query about the request. |  |  |  |  |  |  |  |  |  |  |  |  |
| Date of Request |  |  |  | Requesters Reference No. |  |  |  |  |  |  |  |  |
| Requester Organisation |  |  |  |  |  |  |  |  |  |  |  |  |
| Requesters Address |  |  |  |  |  |  |  |  |  |  |  |  |
| Post Code |  |  |  | Email. |  |  |  |  |  |  |  |  |
| Contact Name |  |  |  | Phone No. |  |  |  |  |  |  |  |  |
| 2. Site Details (Where the work is intended to be carried out) The Requester completes this section providing details of the valid Site address: Post Code should be provided by the Requester where known. Where not available the requester shall provide a valid ordnance survey grid reference number. The MPRN or connections quotation reference number must be provided by the Requester, unless it is an existing service without an MPRN issued, in which case the Gas Supplier/Shipper will generate a number once they have ensured that service pipe is ‘live’ and that all measures have been undertaken to ensure that an MPRN does not exist and that a duplicate record is not created. |  |  |  |  |  |  |  |  |  |  |  |  |
| Site Name |  |  |  |  |  |  |  |  |  |  |  |  |
| Contact |  |  |  | Phone No. |  |  |  |  |  |  |  |  |
| Site Address |  |  |  |  |  |  |  |  |  |  |  |  |
| Post Code |  |  |  | O.S. Grid Ref No: |  |  |  |  |  |  |  |  |
| MPRN |  |  |  | Connections quotation reference number ¹ |  |  |  |  |  |  |  |  |
| Status report from Requester |  | No Gas at ECV No ECV |  | Energy Required |  |  |  |  |  | SPEV= …………..kWh |  |  |
| 3. Information Required The requester completes this section identifying the information required. |  |  |  |  |  |  |  |  |  |  |  |  |
| Is this request made as part of smart metering Yes No |  |  |  |  |  |  |  |  |  |  |  |  |
| Pressure Information Required |  |  | Yes No |  |  | Service Pipe Status Live / Dead Check Undertaken: |  |  |  |  |  | Yes No |
| Capacity Information Required |  |  | Yes No |  |  | Live / Dead Reference Number:² |  |  |  |  |  |  |
| Available ECV Details Required.³ ¹ Where a new service pipe has been requested, the ‘Connection Quotation Reference Number’ must be provided as part of the GT1 Application. ² Where a ‘Live/Dead’ Check has been undertaken by the client, the ‘Live/Dead’ reference number must be provided. ³ If the Applicant requires the ‘ECV Details’, (when available) the Applicant must indicate this in their application. The ECV details, should they be available will be confirmed in the additional information/comments box. |  |  | Yes No |  |  | New Service Existing Service |  |  |  |  |  | Yes No Yes No |

| 4.essential Network Information GT completes this section. |  |  |  |  |  |  | GT’s Request ref no: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Service pipe status |  |  | Live Dead Planned Quoted |  |  |  | MPRN: |  |  |  |
| Service pipe status planned follow up work |  |  |  |  | Fix ECV Open Valve Relay Service Pipe |  |  |  |  |  |
| Service Pipe Capacity Nominated Maximum |  |  |  |  | Service pipe energy value confirmed or available |  |  |  | SPEVnom/max*=……….…………kWh |  |
|  |  |  |  |  | Flowrate |  |  |  | Qnom/max*.=……………….……..sm3/h |  |
| Pressure Tier | Design Minimum Pressure DMP |  |  | Lowest Operating Pressure LOP |  | Maximum Operating Pressure MOP |  | Design Pressure DP |  | Design Maximum Incidental Pressure DMIP |
| LP | 19 mbar |  |  | 25 mbar |  | 75 mbar |  | 75 mbar |  | 200 mbar |
| MP35 | 35 mbar |  |  | 35 mbar |  | 185 mbar |  | 2.0 bar |  | 2.7 bar |
| MP65 | 65 mbar |  |  | 75 mbar |  | 250 mbar |  | 2.0 bar |  | 2.7 bar |
| MP105 | 105 mbar |  |  | 105 mbar |  | 1.1 bar |  | 2.0 bar |  | 2.7 bar |
| MP180 | 180 mbar |  |  | 180 mbar |  | 1.6 bar |  | 2.0 bar |  | 2.7 bar |
| MP270 | 270 mbar |  |  | 280 mbar |  | 2.0 bar |  | 2.0 bar |  | 2.7 bar |
| IP | ………….bar |  |  | ………….bar |  | ………….bar |  | 7.0 bar |  | 9.31 bar |
| Other | …………. mbar/bar* |  |  | …………. mbar/bar* |  | ………… mbar/bar* |  | ………… .mbar/bar* |  | ………. mbar/bar* |
| Additional Information/Comments: |  |  |  |  |  |  |  |  |  |  |
| 5. Application valid date: The GT shall complete this section: The GT1 information provided on this application form is valid for 90 days from the date stated below. The details provided on this GT1 Form in based on the information provided at the time the application was made. The GT will not be responsible for any changes made to site, during the 90day period. |  |  |  |  |  |  |  |  |  |  |
| GT valid Date: |  |  |  |  |  |  |  |  |  |  |

Note: The information provided is solely for the provision of pressure tier information at the location requested.  The provision of capacity information is for indicative purposes only and does not confirm the availability of gas nor does it reserve any capacity.

If the proposed metering pressure is above the DMP of the Network then a separate application for an Ancillary Pressure Agreement will need to be submitted or if the requester has knowledge of a plan to install a booster or compressor they must advise the relevant GT.

Note: Ancillary Pressure Agreements or installing a booster/compressor is not part of the GT1 process.