| # Engineering Justification Paper # Engineering Justification Paper # Kingsferry Bridge Phase 1 Version: Date: Classification: Highly Confidential |  |
| --- | --- |

- Table of Contents

2 Introduction	3

3 Equipment Summary	6

4 Problem Statement	7

4.1 Narrative Real-Life Example of Problem	8

4.2 Spend Boundaries	10

5 Probability of Failure	10

5.1 Probability of Failure Data Assurance	12

6 Consequence of Failure	12

7 Options Considered	13

7.1 Options Cost Details	15

7.2 Options Technical Summery …………………………………………………………………………………………………………………15

7.3 Options Cost Summary Table ……………………………………………………………………………………………………………….15

8 Business Case Outline and Discussion	16

8.1 Key Business Case Drivers Description	16

8.2 Business Case Summary	17

9 Preferred Option Scope and Project Plan	18

9.1 Preferred option	18

9.2 Asset Health Spend Profile	18

9.3 Investment Risk Discussion…………………………………………………………………………………………………………………..18

# Introduction

The sole IP supply pipeline to the Isle of Sheppey crosses the river swale at Kingsferry Bridge. The Island is home to a population of 40,000 residents and 14,953 gas customers, but also has two maximum security prisons. These prisons house male prisoners who, if they were to escape, pose the most threat to the public, the police or national security. The Island also has an open prison and a port.

The bridge was constructed in late 1950’s and opened in 1959 and provides the main rail link to the island and a road crossing. The IP pipeline runs through the bridge structure, under the carriageway, and then through a service tunnel to the other side of the bridge where again it runs under the carriageway to the island. See figure 1 below for a picture of the bridge.

Kingsferry Bridge

The pipeline running from the mainland, through the bridge tunnel to the island, was constructed in the 1960’s and is reaching the end of its serviceable life. The pipeline  is in poor condition. and SGN have been monitoring the situation. The section that runs through the bridge is typical of the pipeline, but due to its proximity within the bridge structure to other stakeholders’ plant and equipment, it poses an extra risk which cannot be ignored.

It is proposed in this paper to replace the highest risk section of this pipeline running through the bridge. This initial phase of work will be supplemented, in later control periods i.e. GD3, with projects intended to replace other sections of the pipeline both upstream, on the mainland, and downstream on the island.

# Equipment Summary

There is currently a 12” steel IP pipeline that is running within the structure of the bridge. This asset is a single supply steel pipe servicing the Isle of Sheppey and is designed to operate at 7 bar gas pressure. The gas main was installed in the 1960s.

The pipe comes off the mainland into the abutment and is laid underneath the decking of the bridge. It then goes down into an access shaft which is 40 metres deep and then into a service tunnel under the River Swale  between the piers  of the bridge. The pipeline follows a mirror route to return to the island side of the bridge.

Figure 2 below shows a network map of the  bridge crossing  and the extent of the system on the Island.

Network Plan

Figures 3 to 6 below show various images of the pipeline within the bridge and access shafts.

Kings Ferry Bridge Tunnel

12’’ steel Gas Main

Kings Ferry Bridge Access Shaft

Kings Ferry Bridge Access Shaft

Pipeline (Right) under carriageway

# Problem Statement

## Why are we doing this work and what happens if we do nothing?

### The pipeline

The IP pipeline that feeds the Isle of Sheppey is in poor condition and a gas escape or failure has the potential to affect all the gas supplies on the Island. With the location of the crossing to the Island, through the bridge, there is also the risk to other infrastructure (including highways, Network Rail and the local water company supplies) if a gas leak was experienced on the pipeline at that section.

The IP pipeline has been repaired several times along its route and is subject to a restriction on its Maximum Operating Pressure. The current restriction is at 4.15bar and is substantially below its design pressure of 7bar.

This proximity to the other infrastructure and issues with access mean that SGN’s normal response to a pipeline leak may not be able to cope with the operational difficulties faced. As such it is likely to need the response of the Pipelines Maintenance Centre (PMC), or a similar specialist response agency, to affect a repair to the pipeline. This was the case on a previous leak on the 11th August 2016 where PMC were contracted to install a ‘SupaTee’ repair clamp on the pipeline.

In 2016, a gas main wall thickness inspection was completed by SGN in the location of the gas escape. The inspection confirmed the pipe wall thickness to be 6.1 mm minimum to 7.2 mm maximum, where 6.1 mm is under the TD3 minimum recommendation of 6.3 mm for this pipeline rating. The most recent leak on the pipeline occurred on 7th October 2019 adjacent to the bridge. This leak was again repaired using a ‘SupaTee’ repair clamp on the pipeline. Fortunately, this leak occurred outside of the section of pipeline within the service tunnel but nonetheless still resulted in the closure of the bridge, railway and road for 48 hours.

### The Bridge

The bridge is owned and operated by Network Rail and is over 60 years old. There are issues accessing the service tunnel with one end inaccessible  due to degradation of the concrete stairwell. There is concern that this degradation will continue such that the integrity of the bridge is compromised and the service tunnel will be no longer be accessible from either end. This raises two issues namely

- Future access to the pipeline is likely to become more difficult . This has logistical and increasing cost implications on pipeline inspection, repair and maintenance activities.

- It is probable that any effective intervention solution on the pipeline should it remain in its current position may exceed the potential remaining operational life of the bridge. Should this be the case we would have no choice but to incur further cost in the future for an additional or alternative intervention.

The tunnel is currently leaking and requires continual pumping to remove approximately 100 gallons of sea water a day. This sea water ingress creates an aggressive atmosphere within the tunnel that is accelerating  the corrosion of the pipe. This corrosive atmosphere is unlikely to improve and increases the risk to the likely numbers of interventions required to the pipeline in situ.

The access issues make it difficult to work on and carry out an intervention to the pipeline. Working in confined spaces to refurbish any  pipeline is  a significant challenge but the  immediate proximity of the  14bar water main , adjacent to the gas main within the service tunnel, provides significant  additional risks to both operatives health and safety and the plant and equipment .

Single Feed

The pipeline is the sole supply to the island. This makes maintenance activities and repairs to the pipeline difficult to effect without putting at risk large numbers of supplies. To mitigate this, when repairs are necessary they have to be undertaken in  live conditions  which  can extend the duration of the works. This in turn affects the other stakeholders and utilities and can, as has occurred in recent leaks, extend any closure of the railway and road crossings. These closures result in significant disruption to the general public and local businesses alike.

### Confined space

Given  the service tunnel is a confined space, there is a need to install controlled ventilation of the working atmosphere in the event of a gas leak in order to manage and mitigate health and safety risks to resources. Access is currently restricted to one pier resulting in significant logistical difficulties and additional time and costs in mobilising plant, equipment and resources for interventions to the pipeline.

Gas Monitoring system

Given the concerns regarding the pipeline and potential gas escapes, the gas monitoring system was installed as a contingency and is now at end of its serviceable life and will need replacing if the pipeline remains in situ. The monitoring system has had multiple failures and is built on legacy and unsupported detection and telemetry equipment.

What happens if we do nothing?

This is the sole IP gas supply to the Isle of Sheppey. The gas main was installed in the 1960s and is reaching the end of its serviceable life. The pipe condition is poor with at least 13 no. known gas leaks attributed to corrosion and failure escapes (4 no. from 1995 to 1999, 1 no. in 2016 and 1 no. in 2019). This pipeline operates in harsh environmental conditions ranging from coastal saltwater to heavy marsh land. The pipeline provides gas supplies to 14,953 customers on the Island , three of which are prison facilities (two high security category A prisons and one open prison) with multiple other industrial/commercial customers.

Leaving this pipeline in place will increase the risk to supplies to the Isle of Sheppey via a through wall corrosion failure on a section of pipeline that potentially cannot be repaired. As with the most recent gas escape, any leak would close both the railway and road crossings of the bridge and could stop the bridge being lifted  to accommodate traffic on the river.

If we do nothing, the pipe will continue to deteriorate and will fail and will result in significant dependant infrastructure and 14,953 customers losing their gas supply.

What is the outcome that we want to achieve?

The project looks to safeguard the supply to customers downstream of the crossing and the security of the local network. We will put in place a replacement crossing and decommission the original asset. It will also enable SGN to start the securing easements for further replacement works, to be installed after GD2, and ensure that practical access will be available for future phases of the work.

How will we understand if the spend has been successful?

The spend will be deemed successful when the project removes the need for any further site inspections by SGN resources within a confined space and potentially remove costs for access rights to the service tunnel. Also, future gas escapes will be prevented.

## Narrative Real-Life Example of Problem

Figures 3 to 6 above show the condition of the service tunnel and the complexity of working in this restricted environment and confined space. There is also evidence of corrosion of the IP gas main and the steel support gantry in the service tunnel under the Kingsferry Bridge

The IP main is in a confined space with current access points to the asset heavily restricted. As future access to the asset becomes further compromised, difficulties to gain access in an out of hours emergency could lead to catastrophic consequences. Gas leaks in the local environment have resulted in complex repair solutions and third party impacts.

There is an existing gas monitoring system in the tunnel to detect the present of gas. This did cease working for a period of 2 weeks, during which an engineer was sent to site on a daily basis to monitor and take gas readings until it was repaired and re-established.

There was a gas escape that was identified and repaired on 11th August 2016 using a 12” ‘SupaTee’ and 12” Blank Flange. This work was undertaken by National Grid Pipeline Maintenance Centre.

A further leak was identified on 7th October 2019 with the gas escape location being 5.5m away from the entrance to the south abutment of the bridge. The main in this location is 0.8m deep to pipe cover and is laid in marshland approximately 20m from the tidal River Swale causing the excavation to be constantly waterlogged.

No further pressure reduction was possible with gas escaping at 3.9bar, and the only other option is to turn off the valve with total loss of supply to entire island. The gas escape presents safety issues given its proximity to a live roadway, HGV vehicles trying to enter Ridham Docks, electrified railway line, and street lighting above on bridge

Figure 7 details the two corrosion holes that were found at the 5 o’clock position approximately 150mm apart. One hole was approximately 20mm diameter, the other approximately 10mm diameter.These holes were repaired by means of a 12” ‘SupaTee’ and a blank flange as detailed in Figure 8.

Given the condition of the main and surrounding area, the repair took five days to complete during which time both the road and railway bridge had to be closed for extended periods due to safety concerns. These closures will result in SGN liability for compensation to the affected stakeholders.

Corrosion Holes

.

SupaTee Repair Clamp

## Spend Boundaries

The programme of works included in this project is the initial phase for a multi-phase project to replace the pipeline. Our initial phase will be undertaken in GD2. This spend will be used to replace the existing IP main contained within the bridge and tunnel and to install a new PE main under the River Swale using Horizontal Directional Drilling (HDD) techniques. This project also incorporates funding to  decommission the asset which must  be undertaken  as part of the existing easement agreement with Network Rail.

In order to minimise the expenditure associated with this project, we have extensively used publicly available geotechnical and bore hole data that was instigated for the construction the new River Swale bridge crossing.

The spend of this project will cover:

- Horizontal directional drilling to replace the current pipeline

- Connections into the existing gas network

- Hydrostatic testing and commissioning the new pipeline

- Decommissioning  of the old pipeline

A tender for the works will be issued in 2021 and a plan to complete the works in 2022 at a cost of £4.91m. As part of this project, we will not be spending money on reconfiguring or upgrading the network.  Prior to GD2 we have undertaken feasibility studies and have commenced  outline design and engagement with  all the relevant stakeholders (Local Authority, Landowner and Environmental Agency) and will consult on the project up to the  summer 2020.

Expenditure and Workload

| Southern Crossings | Southern Asset Population | GD2 Proposed Workloads | Total GD2 Period Funding £m |
| --- | --- | --- | --- |
| Tunnels | 3 | 1 | £4.91m |

During GD3, we anticipate further phases of work to continue replacing the downstream system.

# Probability of Failure

The probability of failure of this asset is high. The asset is a steel pipe and subject to corrosion and a poor cathodic protection system has further added to the deterioration of the asset. The continuing issues with the location and operation of the asset will accelerate further deterioration and could lead to further gas escapes.

Background

The failure rate and deterioration applied to calculate the CBA is consistent with the NARMs methodology. The key principle adopted in the methodology to facilitate the assessment of risk are:

Asset health equates to the probability that the asset fails to fulfil its intended purpose and thus gives rise to consequence for the network.

The consequences can be assessed in monetary terms

The risk is determined from the product of the number of failures and the consequence of those failures

Failure rate

In the NARM framework ‘failure rate’ is used to calculate the Probability of Failure. The failure rate gives the rate of occurrence (frequency) of failures at a given point in time and may also include an age/time variable, known as asset deterioration, which estimates how this rate changes over time. The failure rate can be approximated by fitting various parametric models to observed data to predict failures now and in the future. Therefore, data that contributes towards monetised risk value has been thoroughly reviewed for each system under this investment.

Failure modes

In the NARMs methodology the failures are categorised into different Failure Modes. Below is list of all failure modes considered in the methodology and any data modification made to the model.

Release of Gas - relating to the failure of a pressure containing component on site leading to an unconstrained release of gas within and possibly off the site

General failure - relating to other failures not leading to either a safety, environmental or gas supply related consequence.

Table 2 NARMS Failure rates

| ST IP Band F Failures |  |  |  |
| --- | --- | --- | --- |
|  | FY21 (failures/km) | FY71 (failures/km) | Total Predicted Failures (50 years) (failures/km) |
| Baseline | 0.017573 | 0.205481793 | 3.765992594 |
| Outcome | 0.017573 | 0.03542704 | 1.61310637 |

The primary protection of this asset is in the form of  pipe wrapping, coating  and cathodic protection.  The wrapping and coating  on the IP pipe in the environment of the Kingsferry Bridge has deteriorated, with corrosion of the asset occurring. Failure to replace this pipe will eventually lead to catastrophic failure and a major incident.

This main has had five previous leaks in 1995, 1998, 1999, 2016 and 2019. These leaks related to corrosion and joint failure but not within the actual tunnel itself. If such leaks occur again in the same locations, they could be repaired. If the leak is within the actual tunnel itself there is a possibility that an effective repair could not be made.

The condition of the pipe continues to deteriorate and we have continued to manage the risk and prevailing conditions at the most effective cost in order to maintain security of supplies. This main needs further financial investment over and above normal Opex costs.

In order to avoid a catastrophic failure and consequential loss of supply, investment is required in GD2 to replace the main. Failure to obtain this investment in GD2 will result in inevitable replacement on failure at a later date at potentially a much higher cost in terms of risk to safety, investment and reputation.

Table 3 - C55 Output Kings Ferry Bridge

This table is showing the ongoing monetised risk associated with this pipe without intervention.

| Kings Ferry Bridge Without Intervention |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| PON | Length (km) | Carbon | Finance | Health & Safety | Customer | Total |
| 115873409 | 0.008 | £9,137.12 | £113.71 | £6.52 | £402.88 | £9,660.23 |
| 115873410 | 0.016 | £18,274.24 | £227.41 | £13.05 | £805.76 | £19,320.46 |
| 114480547 | 0.13 | £148,478.19 | £1,847.73 | £106.02 | £6,546.82 | £156,978.76 |
| 114480546 | 0.048 | £54,822.71 | £682.24 | £39.15 | £2,417.29 | £57,961.39 |
| 114480545 | 0.126 | £143,909.63 | £1,790.88 | £102.76 | £6,345.38 | £152,148.64 |
| 115694937 | 0.106 | £121,066.83 | £1,506.61 | £86.45 | £5,338.18 | £127,998.06 |
| Total | 0.434 | £495,688.71 | £6,168.57 | £353.96 | £21,856.31 | £524,067.55 |

Table 4 - C55 Output Kings Ferry Bridge

This table is showing the ongoing monetised risk associated with this pipe with intervention.

| Kings Ferry Bridge with Intervention |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| PON | Length (km) | Carbon | Finance | Health & Safety | Customer | Total |
| 115873409 | 0.008 | £275.23 | £29.86 | £2.60 | £190.16 | £497.84 |
| 115873410 | 0.016 | £550.45 | £59.72 | £5.19 | £380.31 | £995.68 |
| 114480547 | 0.13 | £4,472.44 | £485.21 | £42.20 | £3,090.04 | £8,089.90 |
| 114480546 | 0.048 | £1,651.36 | £179.16 | £15.58 | £1,140.94 | £2,987.04 |
| 114480545 | 0.126 | £4,334.82 | £470.28 | £40.91 | £2,994.97 | £7,840.98 |
| 115694937 | 0.106 | £3,646.76 | £395.64 | £34.41 | £2,519.57 | £6,596.38 |
| Total | 0.434 | £14,931.05 | £1,619.87 | £140.90 | £10,315.99 | £27,007.81 |

## Probability of Failure Data Assurance

Continued and increased frequency of gas escapes are inevitable. Whilst records are incomplete, there have been at least 5 no. known gas leaks attributed to corrosion and failure escapes. We estimate a minimum of one leak at least every 5 years going forward.

- 3 x no. from 1995 to 1999, 1 x no. in 2016, 1 x no. in 2019

- Pipe thickness testing

- CP tests

There is a gas monitoring detection system (which itself is at end of life) in the service tunnel which operates 24 hours a day and will provide alerts should an uncontrolled release of gas occur. Annual inspections of the pipeline are carried out with the most recent being completed in early 2019.

# Consequence of Failure

The failure modes for this pipe relate to the failure of the pipe wall due to corrosion and failure of the coating, wrapping and the pipe support brackets. These modes are also impacted by water ingress in the tunnel which affects the atmospheric conditions. Failure of the access shaft stairs would result in inaccessibility of the pipeline.

Loss of Supply to Customers

Access to the asset within the service tunnel is becoming increasingly difficult, any asset failure would have all the potential requirements for an environmental incident (fuel, air and ignition source). While the incident could be controlled by closure of inline stream valves, disruption and loss of supply to 14,953 customers  would be a real possibility.

Three of these customers are prison facilities including two maximum security prisons. These prisons house male prisoners who, if they were to escape, pose the most threat to the public, the police or national security. The Island also has an open prison and a port along with multiple other industrial/commercial customers. These are critical locations which cannot lose a gas supply. Should failure of this asset occur the potential impact would be high as there is currently no other gas supply to the Isle of Sheppey.

Safety Impact of Failure

The consequence of failure in a confined space would be extremely high with the potential for a significant health and safety risk to the general public, the bridge operator and employees of SGN. At present there are access restrictions to the service tunnel that would impact response times in the event of any gas escape.

Environmental Impact

Due to the location of the IP main combined with the environmental operating conditions, any failure would lead to the probable uncontrolled release of gas within a confined space. In the event of an uncontrolled release of gas (1inch diameter hole) a total of 1,508 scm/h will be released. The railway bridge remains in operation to and from the Isle of Sheppey. These services would be severely impacted with significant disruption to businesses and the general public caused by delays and/or loss of use during any major event.

# Options Considered

### SGN 4r Strategy

When considering this intervention, we have done so following our 4r strategy. This strategy is designed to maximise the asset life and minimise the capital expenditure of any intervention and in doing so sets out an order when considering the intervention type. This consideration is key in delivering customer value and focuses on the lighter intervention options of repairing and refurbishing the asset before considering more severe interventions such as component replacement and full rebuild. See Figure 9 below for an illustration of our 4r strategy:

SGN 4r Strategy

From our annual inspections and analysis of CP readings on the rest of the pipeline, SGN consider the existing pipeline to be in poor condition. This is largely due to the proximity of the crossing to a saltwater body of water and ground conditions in the area.

Whilst SGN have been monitoring the situation for some time, a survey commissioned by SGN in 2018 has recommended replacement of the pipeline and crossing. The options detailed in Table 5 were considered to secure gas supplies for the future: -

Table 5 -  Options Considered

| Option | Description | Comment |
| --- | --- | --- |
| Do Nothing | No replacement, repair only | Discounted due to the current condition of main and being a single feed to the Island. |
| Repair on Failure | Reactive response to repair | Discounted due to the increasing potential for significant gas escapes and the possibility that a repair could not be undertaken due to the deteriorating conditions in the service tunnel. This would result in extended durations when the single feed to the Island would be isolated. |
| Replace on Failure | Reactive response to replacement of main within the existing bridge on failure | Discounted due to the increasing potential for significant gas escapes and the complexity of undertaking the replacement works in the service tunnel. Due to space within the bridge and the existing pipe, it is not possible to take the old pipe out and install a new one. Also, the condition and structure of the bridge is not good. The tunnel is leaking water at a rate of 100 gallons a day. This would result in extended durations when the single feed to the Island would be isolated. |
| Pre-Emptively Replace | Replacement of main via horizontal directional drill | Replacement of the IP main from the North East side of the River Swale to the City Gate at Cowstead Corner, progressing to the Brielle Way City Gate. This will improve and secure gas distribution for the medium to long term future and mitigate the risk of a catastrophic asset failure. |
| Other Considered Option | Replacement of main from the Isle of Grain to Sheerness docks via horizontal directional drill | The option of laying an IP main from the Isle of Grain to Sheerness Dock was considered however discounted as not as cost effective as the pre-emptive replacement solution and very likely Peels Ports and other interested parties would reject this this option due to their development plans at the docks. |

The project scope has already been determined with SGN Asset Management and identified in this document. It has been recommended that the SGN IP gas main servicing the Isle of Sheppey, is replaced in its entirety from the south side of the Kingsferry Bridge, across the River Swale.

This solution will add value by;

- Improved safety to users and SGN operatives

- Increase gas supply resilience Secure future gas supply network

- Secure easements now prior to development

- Reduce operational cost

While this work is being undertaken existing below ground installations within the southern area would be maintained and repaired where required. In the interim period SGN will develop a viable contingency plan that can be utilised in the event of a major failure to improve safety to users and SGN operatives, increase gas supply resilience and secure the gas supply network.

## Replace on failure

The current structural integrity of the asset would compromise security of supply for the network and provide Health and Safety concerns for both the public and SGN employees. SGN would not be permitted to allow its employees into a hazardous confined space where we know there is an uncontrolled release of gas.

The technical detail of the option i.e. capacity, system rating, availability etc.

The existing pipe runs from the Southeast side of the River Swale crossing the Kingsferry Bridge via a service tunnel under the river to an existing SGN valve. In a situation where replacement of a section of the existing 12” steel IP main that is running within the structure of the Kingsferry Bridge is required, repair collars and/or the installation of new pipework sections will be the only viable option.

The pipeline will need to be inspected locally along its length to validate any replacement technique and confirm the impact the method of working may have on other adjacent infrastructure. Access arrangements will need to be improved to undertake any significant replacement work and forced ventilation systems will need to be mobilized to enable any intrusive working requirements. The access shafts would need to be fully scaffolded should the repair be in the vertical sections of the pipeline and to support ventilation and material access and egress.

The existing supply will need to be isolated from the network either side of the bridge for the duration of replacement works resulting in significant disruption to gas customers. The railway line and the bridge crossing will be closed for the duration of the gas leak resulting in compensation to Network Rail and significant disruption to the general public.

The basis for the cost estimate/unit cost

SGN consider a meaningful cost estimate cannot be prepared given the vast range of scope of work uncertainties and the significant range of potential commercial impacts.  These requirements are fully dependent upon the scale and location of the gas escape that could include but not be limited to

- Significant forced ventilation and fully staged access and support scaffolding systems

- Unknown temporary works and pipe support requirements

- Specialist shot blasting, wrapping and coating and pipe replacement resources

- SGN inspection and operations teams and specialist repair teams in attendance

- Unknown compensation liabilities to third parties

The perceived benefits of the option

There are no perceived benefits to this option as it would result in

- Significant Health and Safety risk to SGN employees and contractors mobilized to undertake the replacement works

- Loss of supply to potentially 14,953 customers for an uncontrolled extended period

- Significant disruption to the general public and third parties

- Significant compensation risk to Network Rail, Peel Ports and other impacted third parties

Delivery timescales

Subject to the volume and nature of replacement works required after a significant failure, there  could be a loss of supply for potentially several weeks.

Key assumptions made

- The failure is isolated within a section of pipeline and the specialist materials and resources to undertake the works will be readily available

- The ability to undertake an effective replacement assumes that the pipeline condition in the area of repair is capable to accept a replacement or cut in pipe insert.

Any other items that differentiate the option from the others considered

This solution would result in the need to reactively mobilise continued replacement of sections of the pipeline after failure

## Repair on failure

The technical detail of the option i.e. capacity, system rating, availability etc.

The current structural integrity of the asset would compromise security of supply for the network and provide Health and Safety concerns for both the public and SGN employees. SGN would not be permitted to allow its employees into a hazardous confined space where we know there is a risk of  an uncontrolled release of gas.

The pipeline will need to be inspected locally along its length to validate any repair technique and confirm the impact the method of working may have on other adjacent infrastructure. Access arrangements will need to be improved to undertake any significant repair work and forced ventilation systems may need to be mobilized to enable any intrusive working requirements. The access shafts would need to be fully scaffolded should the repair be in the vertical sections of the pipeline and to support ventilation and material access and egress.

Depending on the location of the failure it may not even be  possible to complete a repair, nonetheless the existing supply will need to be managed and potentially isolated from the existing network either side of the bridge for the duration of repair works resulting in significant disruption to gas customers. The railway line and the road will be closed for the duration of the gas leak resulting in significant disruption to the general public, local businesses and payment of compensation to Network Rail.

The basis for the cost estimate/unit cost

SGN consider a meaningful cost estimate cannot be prepared given the vast range of scope of work uncertainties and the significant range of potential commercial impacts. These requirements are fully dependent upon the scale and location of the gas escape that could include but not be limited to

- Significant forced ventilation and fully staged access and support scaffolding systems

- Unknown temporary works and pipe support requirements

- Specialist shot blasting, wrapping and coating resources

- SGN inspection and operations teams and specialist repair teams in attendance

- Unknown compensation liabilities to third parties

The perceived benefits of the option

There are no perceived benefits to this option as it would result in

- Significant Health and Safety risk to SGN employees and contractors mobilized to undertake the replacement works

- Loss of supply to potentially 14,953 customers for an uncontrolled period

- Significant disruption to the general public and third parties

- Significant compensation risk to Network Rail, Peel Ports and other impacted third parties

Delivery timescales

Repair on the asset in a confined space would be difficult to affect and could result in loss of supply of up to a week. Should the repair be complex this could increase to several weeks and depending on the location of the failure it may not possible to complete a repair.

Key assumptions made

- The failure is isolated within a section of pipeline

- The ability to undertake an effective repair assumes that the pipeline condition in the area of repair is capable to accept a repair clamp.

- The specialist materials and resources to undertake the works will be readily available

Any other items that differentiate the option from the others considered

This solution would result in the need to continually react to gas escapes to repair the pipeline after failure.

## Pre-Emptively Replace

The technical detail of the option i.e. capacity, system rating, availability etc.

Two options were considered to pre-emptively replace the 12” steel IP main that is running within the structure of the Kingsferry bridge with a new supply via horizontal directional drilling (HDD) techniques.

- Option 1 - Crossing the River Medway from the Isle of Grain to the Isle of Sheppey

- Option 2 - Crossing the River Swale from Kent to the Isle of Sheppey

Option 1

A connection from the gas network on the Isle of Grain to the Isle of Sheppey was considered by SGN as detailed in Figure 10 below

Indicative Crossing – Isle of Grain to the Isle of Sheppey

This option was discounted for the following key reasons

- The crossing would be at least 2.5 to 3 km and challenge to the limits of HDD techniques (typically 1.5 km)

- Ground conditions are unknown and would require an extensive detailed site investigation

- The viable crossing intersects a busy shipping lane is very likely to be rejected by Peel Ports

- The drill and reception sites for the HDD are within commercial development land for car imports on Sheppey and will interface with significant infrastructure on the Isle of Grain

- The main from this crossing to the Sheppey side of the Kingsferry Bridge will still need to be replaced

It was therefore considered that this solution would not be as cost effective as a crossing of the River Swale from Kent to the Isle of Sheppey

Option 2

The scope of the works is to install a new SDR9 HDPE pipeline under the River Swale by Horizontal Directional Drill techniques. Planning this intervention means we can maintain supply to customers on the Island.

This HDD main needs to be installed at a depth of 17m with the drilling shot being circa 370m in length. As detailed in Figure 11, the sites will need to extend in both directions to accommodate pipeline stringing and accommodation works.  The entry and exit points of the HDD will connect via operational valves onto the existing SDR 11 main. An additional 300m of the open cut is also necessary to connect onto the existing 12” IP via welded under pressure tee via stopple operations. The main within the bridge will be decommissioned as required by the terms of the Network Rail easement agreement.

Indicative Crossing – Isle of Grain to the Isle of Sheppey

The basis for the cost estimate/unit cost

The cost estimate has been established from various sources as summarised in Table 6 below

| Site Investigation and Outline Design | Scope of work established from detailed discussions with SGN Framework Service Providers. Proposal estimates provided following a feasibility study to establish route and technique options. |
| --- | --- |
| Feasibility/Planning and Detailed Design |  |
| PE Fittings cost | Indicative material schedules from feasibility study and connection details outline with pricing from SGN construction cost database |
| Steel Fittings cost |  |
| Management and set up costs | Forecast costs from outline project programme |
| Welding cost to project | Forecast cost estimate from SGN construction cost database |
| Lay and connection costs | Forecast costs from detailed discussions and budget proposals from HDD specialists |
| Other ancillary costs | Forecast cost estimate from SGN construction cost database |

The perceived benefits of the option

Whilst the risks to existing pipeline will remain during the construction phase of this project, once the new pipeline is installed the perceived benefits of this option are considered to be

- Planning this intervention means supply to customers on the Island can be managed and maintained

- Enhanced resilience and security of supply in the local network by mitigating the risk of gas supply failure with improved network pressure control and resilience to ensure minimum disruption to customers

- The significant Health and Safety risk to SGN employees and contractors mobilized to undertake future repair or replacement works will be mitigated by removal of an unsafe working environment from SGN operatives responding to a fault

- Mitigate future significant disruption to the general public and third parties

- Mitigate future significant compensation risk to Network Rail, Peel Ports and other impacted third parties

- The removal of an existing IP steel main from within a third-party structure.

- Enable SGN to expedite further projects to provide capacity and resilience for future development in the area

Delivery timescales

- Planning Consultation and design (ongoing) - 6 months

- Procurement of long lead materials and mobilisation to site – 3 to 6 months

- Construction and Commissioning – 6 months

- Overall project – 12 months

Any other items that differentiate the option from the others considered

This project solution has been developed following a feasibility study that engaged various technical specialists ( including HDD specialist LMR Drilling UK Ltd and planning and environmental specialist Dalcour McLaren) to establish a design and route that was both technically and commercially viable. This study also identified the necessary areas of engagement with all stakeholders and third parties and has been confirmed as feasible.

## Pre-Emptively Repair

A pre-emptive pipeline refurbishment option was considered but it is not possible to identify the full scale of potential pipe integrity problems by remote methods or pipeline inspection pigging techniques in advance of the works. Inspection and refurbishment would as a minimum involve the removal and reapplication of coating , pipe repairs and/or replacement of sections of pipe and replacement of the existing support brackets.

Shot blasting or intrusive abrasion techniques would be required just to remove the existing coatings and enable some form of indicative inspection. Given the concern over the integrity of the pipe it would not be acceptable from a health and safety perspective, to both SGN employees and third parties, to undertake this inspection work on the live gas main nor would SGN be permitted to allow its employees into a hazardous confined space where we know there is a potential of an uncontrolled release of gas if the pipe was to fail.

The current structural integrity of the bridge cannot be confirmed and the value in refurbishing our asset insitu could be compromised by external factors. The current bridge structure has continued to deteriorate and Network Rail have not confirmed the long term future of the bridge. This uncertainty and the prevailing conditions in the environ of the bridge structure could further complicate or even prevent any insitu repair in the future.

A repair on the asset (depending on the location of the failure, it may not even be possible to complete a repair) in a confined space would be difficult to affect and would result in loss of supply of up to a week. If it was indeed possible, a full refurbishment of the pipeline would take many months .

Given these factors any refurbishment option would therefore require the gas main to be isolated and gas supply to the Isle of Sheppey suspended for a significant and uncontrolled amount of time. Notwithstanding the construction uncertainties, this isolation is neither operationally or commercially viable and therefore the option to refurbish the pipeline was discounted.

The technical detail of the option i.e. capacity, system rating, availability etc.

Not considered viable by SGN

The basis for the cost estimate/unit cost

SGN consider a meaningful cost estimate cannot be prepared given the vast range of scope of work uncertainties and the significant range of potential commercial impacts.

## Do nothing

In order to maintain compliance with licenses, regulations and  legislation there is no option for SGN to do nothing. The minimum SGN would need to provide for is the likelihood of increasing reactive responses to repairs on failure of the pipeline with the need to provide for the increasing risk of a catastrophic failure of the network.

## Options Technical Summary Table

Table 7  – Options Technical Summary

| Option | First Year of Spend | Final Year of Spend | Volume of Interventions | Equipment / Investment Design Life | Total Cost |
| --- | --- | --- | --- | --- | --- |
| Replace on Failure |  |  |  |  |  |
| Repair on Failure |  |  |  |  |  |
| Pre-Emptively Replace | 4.91 | 0 | 1 | 40 | 4.91 |
| Pre-Emptively Repair |  |  |  |  |  |
| Do Nothing |  |  |  |  |  |

## Options Cost Summary Table

Table 8 – Cost Summary

| Option | Cost Breakdown | Total Cost (£m) |
| --- | --- | --- |
| Replace on Failure | The current structural integrity of the asset would compromise security of supply for the network and provide Health and Safety concerns for both the public and SGN employees. SGN would not be permitted to allow its employees into a hazardous confined where we know there is an uncontrolled release of gas. The cost of £23.9m is constructed of loss of supply to 14,953 customers = £16.8m, Societal cost £0.5m, Network rail compensation £1.4m, Risk £168k and Replacement £5.0m. | 23.9 |
| Repair on Failure | The current structural integrity of the asset would compromise security of supply for the network and provide Health and Safety concerns for both the public and SGN employees. SGN would not be permitted to allow its employees into a hazardous confined where we know there is an uncontrolled release of gas. The cost of £23.9m is constructed of loss of supply to 14,953 = £16.8m, Societal cost £0.5m, Network rail compensation £1.4m, Risk £168k and Replacement £5.0m. | 23.9 |
| Pre-Emptively Replace | This is our preferred replacement option and established using actual market rates and proposals Cost Head; Estimate £. Site Investigation/Feasibility/Planning and Design; £430,000. PE Fittings cost; £320,000. Steel Fittings cost; £480,000. Management and set up costs; £320,000. Welding cost to project; £40,000. Lay and connection costs; £3,130,000. Other ancillary costs; £190,000. Total; £4,910,000. | 4.91 |
| Pre-Emptively Repair | The current structural integrity of the asset would compromise security of supply for the network and provide Health and Safety concerns for both the public and SGN employees. SGN would not be permitted to allow its employees into a hazardous confined space where we know there could be a potential uncontrolled release of gas if the pipe fails. |  |
| Do Nothing | This would increase the risk of catastrophic failure of the network, together with an increased risk from third party damage to our main. | 102 |

# Business Case Outline and Discussion

SGN have commenced a programme to investigate and determine a route for the works. Following this initial investment there is an ongoing assessment of the route to determine the best approach and to mitigate/minimise disruption to stakeholders, natural wildlife and fauna. The programme will continue through to construction in GD2 to ensure a high level of security to the network and removal of the current defective asset securing the following opportunities;

- Enhanced resilience and security of supply in the local network by mitigating the risk of gas supply failure.

- Removal of an unsafe working environment from SGN operatives responding to a fault

- The removal of existing IP steel main considered at the end of its serviceable life

- Reinforce supply security of the local network with improved network pressure control and resilience to ensure minimum disruption to customers

- Reduced operational and reputational risk

- Enable SGN to expedite further projects to provide capacity and resilience for future development in the area

- The removal of existing IP steel main from within a third-party structure.

- Remove the need for any further site inspections by SGN resources within a confined space

The likelihood of a failure in the near future remains high and has a potential to cause a major disruption to supply to the Isle of Sheppey. There is also a high potential for a significant health and safety risk to SGN operatives, third parties and the general public. Strategic Planning will continue to provide contingency plans for the interim period prior to installation of the permanent solution.

It is impossible to accurately predict when this main will fail. The probability of failure will likely be the pipe support brackets as they are heavily corroded and take the full weight of the pipe. The consequences of failure will be catastrophic and will create a major incident and loss of supply to a population of 40,000 and 14,953 gas customers.

This is the only gas supply to the Isle of Sheppey. If the pipe fails in the tunnel it will result in road closures of the two main crossings onto the Isle. This will impact rail and supply of goods and services to the Isle.

## Key Business Case Drivers Description

Table 9 – Summary of Key Value Drivers

| Option No. | Desc. of Option | Key Value Driver |
| --- | --- | --- |
| 1 | Replace on Failure | The current structural integrity of the asset would compromise security of supply for the network and provide Health and Safety concerns for both the public and SGN employees. SGN would not be permitted to allow its employees into a hazardous confined where we know there is an uncontrolled release of gas. Identified as significant risk remains to SGN network, employees, third parties and customers |
| 2 | Repair on Failure | The current structural integrity of the asset would compromise security of supply for the network and provide Health and Safety concerns for both the public and SGN employees. SGN would not be permitted to allow its employees into a hazardous confined where we know there is an uncontrolled release of gas. Identified as significant risk remains to SGN network, employees, third parties and customers |
| 3 | Pre-Emptively Replace | Approve a GD2 project spend of £4.91m Capex for the replacement of the existing IP gas main crossing the Kingsferry Bridge to the Isle of Sheppey. - Enhanced resilience and security of supply in the local network by mitigating the risk of gas supply failure. - Removal of an unsafe working environment from SGN operatives responding to a fault - The removal of existing IP steel main considered at the end of its serviceable life - Reinforce supply security of the local network with improved network pressure control and resilience to ensure minimum disruption to customers - Reduced operational and reputational risk - Enable SGN to expedite further projects to provide capacity and resilience for future development in the area - The removal of existing IP steel main from within a third-party structure. - Remove the need for any further site inspections by SGN resources within a confined space |
| 4 | Pre-Emptively Repair | The current structural integrity of the asset would compromise security of supply for the network and provide Health and Safety concerns for both the public and SGN employees. SGN would not be permitted to allow its employees into a hazardous confined where we know there is an uncontrolled release of gas. Identified as significant risk remains to SGN network, employees, third parties and customers |
| 5 | Do Nothing | This is not an option to be considered, If the work to replace the existing IP gas main is not undertaken, there is a high risk that there will be a major gas escape in the SGN IP gas main that runs through the Kingsferry Bridge service tunnel that will result in a reduced or no gas supply to customers or a gas supply failure. Identified as significant risk remains to SGN network, employees and customers |

Table 10 – Summary of CBA Results

| NPVs based on Payback Periods (absolute, £m) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Option No. | Desc. of Option | Preferred Option (Y/N) | Total Forecast Expenditure (£m) | Total NPV | 10 Yrs | 20 Yrs | 30 Yrs | 45 Yrs |
| 1 | Replace on Failure | N |  |  |  |  |  |  |
| 2 | Repair on Failure | N |  |  |  |  |  |  |
| 3 | Pre-Emptively Replace | Y | 4.91 | 101.65 | 18.22 | 48.07 | 69.94 | 94.97 |
| 4 | Pre-Emptively Repair | N |  |  |  |  |  |  |
| 5 | Do Nothing | N | £192.50 | -£102.96 | -£34.57 | -£59.05 | -£78.91 | -£98 |

## Business Case Summary

SGN is requesting an approved expenditure of £4.91m over the GD2 period. This spend is required to enable SGN to secure and maintain its gas supply to the Isle of Sheppey. The works shall be managed and delivered by Southern Maintenance Operations, using direct and contract resources. This is currently part of an ongoing programme scheduled to be completed over GD2.

Table 11 - Business Case Matrix

|  | Option Replace on failure | Option Repair on failure | Option Pre-emptively replace | Option Pre-emptively repair | Option Do nothing |
| --- | --- | --- | --- | --- | --- |
| Capex (£m) |  |  | 4.91 |  |  |
| Number of Interventions |  |  | 1 |  |  |
| Carbon Emission Savings (2040 total, £m) |  |  |  |  |  |
| Explosion Risk Reduction (2040 total £m) |  |  |  |  |  |
| Avoided Maint. (2040 total £m) |  |  |  |  |  |
| NPV (2040 £m) |  |  |  |  |  |

# Preferred Option Scope and Project Plan

## Preferred option

The preferred option would be to initially replace the IP gas main from the south side of the Kingsferry Bridge to a connection across the River Swale using horizontal directional drilling techniques. This is the only assured method to both safeguard the integrity of the gas distribution network and ensure improved health and safety for the public and operatives of SGN.

## Asset Health Spend Profile

Table 12 - Asset Health Spend Profile (£m)

| Asset Health Spend Profile (£m) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Pre GD2 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | Post GD2 |
| 0.45 | 4.91 | 0 | 0 | 0 | 0 | 0 |

The identified spend pre-GD2 is not part of this project. This spend profile is based on the ability to deliver a programmed replacement of the IP gas main servicing the Isle of Sheppey Kent in its entirety from the south side of the Kingsferry Bridge and within the service tunnel that crosses the River Swale.

## Investment Risk Discussion

The investment for this project is controlled by a tendered contractor event to ensure a high-level confidence will be seen. This allows a fully forecastable level of investment with fully understood market factors and pressures.

The table below identifies risks outside of our control that have the potential to impact this project, detailed within the cost benefit analysis template are the full mitigation and controls for these events.

| Risk Description | Impact | Likelihood | Mitigation/Controls | Comments |
| --- | --- | --- | --- | --- |
| Availability of Contractors | MEDIUM | <=20% | Due to the size and complexity of this project there are a smaller number of contractors with the competency to carry out this work. | Availability of contractors and time scales to complete the works. |
| Unexpected change in legislation | HIGH | <=20% | Agree reopener mechanism with Ofgem to increase or reduce funding as required. | The unexpected cessation of this project would potentially leave an at risk pipe contained within the network. Safety is our number one priority; therefore, we would continue to carryout reactive repairs to this pipe to ensure safety of our customers. Replacement of this pipe would be considered only when a CBA allows this. |
| Brexit impact - road network | LOW | >20% & <=40% | Engage with Highway authorities to plan and optimise the works in lesser congestive zones | Road networks experiencing traffic jams and standstills on major arterial routes |
| Major civil construction programme in [South / Scotland] | LOW | <=20% | Monitor large scale planned projects and market rates of pay | Given the significant nationwide expenditure on other major particularly heavy engineering projects over the relevant period of RIIO-GD2 it is likely there would be an indirect impact on SGN’s supply chain costs. We will look to source relevant data to ascertain the actual levels of increase in the defined period and draw on skilled resource. |
| Impact of major events | LOW | <=20% | Engage with stakeholders to understand future planning arrangements | Development of the Isle of Sheppey and the docks. |

Additional to the above, sensitivity analysis will be produced by Angelo for population in this section.

Appendix

Engineering Justification Paper Checklist

[Enter copy of completed EJP Checklist]

Acronyms

| Acronym | Description |
| --- | --- |
| mA | Milliamps, unit of electrical current |
| PSR | Pressure Systems Regs |
| IP | Intermediate Pressure |
| ST | Steel |
| HDD | Horizontal Drilling Technique |
| GD2 | Gas Distribution determination 2021 – 2026 |